Fantech			November 2016

Canada			US

50 Kanalflakt Way		10048 Industrial Blvd.

Bouctouche, New Brunswick E4S 3M5	Lenexa, Kansas 66215

Canada			United States

Toll Free	800-565-3548	800-747-1762

Website	www.fantech.net	www.fantech.net

E-mail	CANADAsupport@fantech.net	USsupport@fantech.net

Product Guide Specification

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The CSI Construction Specifications Practice Guide.

This section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” after editing this section.

Section numbers and titles are from MasterFormat 2012 Update.

23 72 15

Heat Recovery Ventilator

Specifier Notes:  This section covers Fantech H2800Xi heat recovery ventilators.  Consult Fantech for assistance in editing this section for the specific application.

GENERAL

SECTION INCLUDES

Heat recovery ventilators.

RELATED REQUIREMENTS

Specifier Notes:  Edit the following list of related sections as necessary.  Limit the list to sections with specific information that the reader might expect to find in this section, but is specified elsewhere.  Include section number and title.

Section 23 08 00 – Commissioning of HVAC.

REFERENCE STANDARDS

Specifier Notes:  List standards referenced in this section, complete with designations and titles.  Delete standards not included in the edited section.  Including a standard in this list does not require compliance with that standard.

ANSI/AHRI 1060 – Performance Rating of Air-to-Air Heat Exchangers for Energy Recovery Ventilation Equipment.

ANSI/AMCA 300 – Reverberant Room Method for Sound Testing of Fans.

ASHRAE 84 – Method of Testing Air-to-Air Heat Exchangers.

ASTM A 792/A 792M – Standard Specification for Steel Sheet, 55 % Aluminum-Zinc Alloy-Coated by the Hot-Dip Process.

CSA C22.2, No. 77 – Motors with Inherent Overheating Protection.

CSA C22.2, No. 100 – Motors and Generators.

CSA C22.2, No. 113 – Fans and Ventilators.

CSA C22.2, No. 236 – Heating and Cooling Equipment.

ISO 9001:2008 – Quality Management Systems – Requirements.

NFPA 70 – National Electrical Code (NEC).

UL 723 – Standard for Test for Surface Burning Characteristics of Building Materials.

UL 900 – Standard for Air Filter Units.

UL 1004-2 – Standard for Impedance Protected Motors.

UL 1004-3 – Standard for Thermally Protected Motors.

UL 1004-7 – Standard for Electronically Protected Motors.

UL 1812 – Standard for Ducted Heat Recovery Ventilators.

UL 2111 – Standard for Overheating Protection for Motors.

PREINSTALLATION MEETINGS

Specifier Notes:  Edit preinstallation meetings as necessary.  Delete if not required.

Convene preinstallation meeting [1 week]  [2 weeks] before start of installation of heat recovery ventilators.

Require attendance of parties directly affecting work of this section, including Contractor, Architect, Engineer, installer, and manufacturer’s representative.

Review materials, preparation, installation, adjusting, demonstration, protection, and coordination with other work.

SUBMITTALS

Specifier Notes:  Edit submittal requirements as necessary.  Delete submittals not required.

Comply with Section 01 33 00 – Submittal Procedures.

Product Data:  Submit manufacturer’s product data, including preparation and installation instructions.

Shop Drawings:  Submit manufacturer’s shop drawings, including plans, elevations, sections, and details.

Wiring Diagrams:  Indicate wiring for each item of equipment and interconnections between items of equipment.

Include manufacturer’s names, model numbers, ratings, power requirements, equipment layout, device arrangement, complete wiring point-to-point diagrams, and conduit layouts.

Manufacturer’s Certification:  Submit manufacturer’s certification that heat recovery ventilators comply with specified requirements and are suitable for intended application.

Manufacturer’s Project References:  Submit manufacturer’s list of successfully completed air handling unit projects, including project name and location, name of architect and engineer, and type and quantity of air handling units furnished.

Installer’s Project References:  Submit installer’s list of successfully completed air handling unit projects, including project name and location, name of architect and engineer, and type and quantity of air handling units installed.

Operation and Maintenance Data:

Submit manufacturer’s operation and maintenance manual; including the following:

Operation, maintenance, adjustment, and cleaning instructions.

Troubleshooting guide.

Parts list.

Electrical wiring diagrams.

Provide detailed information required for Owner to properly operate and maintain equipment.

Warranty Documentation:  Submit manufacturer’s standard warranty.

QUALITY ASSURANCE

Manufacturer’s Qualifications:

Manufacturer regularly engaged, for past 5 years, in manufacture of air handling units of similar type to that specified.

ISO 9001 certified company.

Installer's Qualifications:

Installer regularly engaged, for past 5 years, in installation of air handling units of similar type to that specified.

Employ persons trained for installation of air handling units.

DELIVERY, STORAGE, AND HANDLING

Delivery Requirements:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

Storage and Handling Requirements:

Store and handle materials in accordance with manufacturer’s instructions.

Keep materials in manufacturer’s original, unopened containers and packaging until installation.

Store materials in clean, dry area indoors.

Protect materials during storage, handling, and installation to prevent damage.

WARRANTY

Warranty Period:  3 years.

PRODUCTS

MANUFACTURER

Fantech, 50 Kanalflakt Way, Bouctouche, New Brunswick E4S 3M5, Canada. For Canada:  Toll Free 800-565-3548.  Website www.Fantech.net.  E-mail CANADAsupport@systemair.net.

For US: Toll Free 800-747-1762.  Website www.Fantech.net.  E-mail USsupport@fantech.net.

HEAT RECOVERY VENTILATORS

Heat Recovery Ventilators:

Specifier Notes:  Specify required model.  Consult Systemair Inc. for assistance in determining heat recovery ventilator model for the specific application.

Model:  H2800Xi

Indoor, compact, commercial, air handling units.

General:

Each Unit or Group of Units:  Capable of operating in any mode independently or dependently of other systems.

Capable of changing modes with no interruption to system operation.

Listed under CSA C22.2, No. 113/UL 1812.

Wiring:  NFPA 70.

Performance:  As scheduled on the Drawings.

Equip with control systems.

Perform all functions necessary for operation.

Ventilation to Building:  Not to cease in any mode based solely on operational temperature of minus 13 to 104 degrees F (minus 25 to 40 degrees C).

Sound Data:  Measured in accordance with AMCA 300.

Capable of operating at normal condition with specific fan power (SFP) lower than 0.5W/cfm.

Capable of operating in winter and summer conditions without imbalance or loss of ventilation capacity greater than specified in design.

Unit Cabinet:

Cabinet Exterior:  22-gauge sheet galvanized steel, G90 coated with baked powder paint.

Double-Wall Cabinet Interior:

20-gauge sheet galvanized steel, G90.

Seams:  Sealed, requiring no caulking in field.

Insulation within Double Wall:

2.0-inch (50.8-mm) fiberglass.

Flame Spread Index, UL 723:  Not over 25.

Smoke Developed Index, UL 723:  Not over 50.

Fans:

Direct-drive, backward-inclined, motorized impellers.

Fan Motors:

Maintenance-free, permanently lubricated, sealed ball bearings.

Thermal overload protected (TOP).

UL listed to UL 1004-1, 1004-2, 1004-3, 1004-7 and/or UL 2111; CSA C22.2, No. 77 and No.100.

IP Protection:  Class 54.

Electronically commutated “EC” to maximize efficiency at different speeds.

Mounted for quiet operation.

Separate fans for exhaust and supply blowers.

Heat recovery exchanger:

Exchanger Construction:  Corrosion-resistant aluminum alloy, composed of corrugated flat layers that guarantee laminar air flow and low static pressure loss.

Cross-flow construction type.

Free cooling capacity.

Performance:  Certified and listed by AHRI.

Frame Material:  Corner profiles in aluminum and gables in aluminum-zinc sheet steel

Effectiveness of exchanger:  Documented in accordance with ASHRAE 84 and AHRI 1060.

Flame Spread Index, Heat Recovery Exchanger, UL 723:  Not over 25.

Smoke Developed Index, Heat Recovery Exchanger, UL 723:  Not over 50.

Air Filters:

Fresh and exhaust air protected by MERV8 pleated filter constructed to meet UL 900. (Optional MERV13 filters are direct replacement to the MERV8)

Adjustable Monitoring System:  Activates alarm through main controller when pressure drop increase through supply or exhaust filters.

Specifier Notes:  Specify four or five temperature sensors.  Four is standard.

Temperature Sensors:  [Four]  [Five] stainless steel temperature sensors for monitoring supply and exhaust air in and air out, maximizing units efficiency and detecting need for frost prevention.

Electrical 1 phase input voltage:

Electrical Power:  240 VAC, 1 phase, 60 Hz w

Internal Electrical Components:  Factory wired for single-point power connection.

Electrical Box Components:  Accessible without stopping unit or opening doors.

Electrical Box:

Isolated from airflow paths.

Protect integral wires and connections.

Controlled by integral microprocessor controller.

Serviceability:

Access Panel:  Hinged and/or screwed access panel on front of unit.

Heat Recovery Exchangers, Filters, and Motors:  Serviceable from front of unit.

Fan Assemblies:  Mounted on removable base.

Heat Recovery Exchangers and Filters:  Mounted on slide-out rails.

CONTROLS

General:

Corrigo:  Capable of supporting remote controllers, schedule timers, system controllers, centralized controllers, integrated web-based interface, graphical user workstation, and system integration to Building Management Systems via Native BacNET, LonWorks, Modbus via RS 485, Exoline, built-in web, and TCP/IP.

Digital wall controller display.

Controller Communications:  Via common non-polar communications bus.

Control Wiring:  Installed in system daisy-chain configuration from unit to BAS controller and to other units, if applicable.

Network Wiring:  CAT-5e with RJ-45 connection.

Integration with Building Management Systems:

Corrigo in EXO4 System:  Equipped with RS485 port for bus communication via EXOline or Modbus.  Enables controller to be directly integrated with EXO4, Regin SCADA system.

Corrigo Web in a network:

Corrigo directly integrated with foreign SCADA system via Modbus/LON:

Corrigo integrated with foreign SCADA system via Regin EXOopc Driver:

Corrigo Connected to Foreign Protocols:

Controller:  Handle BACnet, Johnson, Trend, and other foreign protocols via EXO communicator.

Corrigo connected to BACnet system:

Schedule Timer:

Corrigo:  Year-base clock function.  Weekly schedule with holiday periods for full year can be set.

Clock:

Automatic summertime/wintertime change-over, individual schedules for each weekday, and separate holiday setting.

Up to 24 individual holiday periods configurable.

Holiday Period:  Anything from 1 day up to 365 days.

Holiday Schedules:  Take precedence over other schedules.

Each Day:  Up to 2 individual running periods.

Pressure Controlled Fans:  Daily individual schedules for normal speed and reduced speed, each with up to 2 running periods.

Up to 5 digital outputs available as timer controlled outputs.  Each with individual week schedules with 2 activation periods per day.

Graphical User Workstation Software:

E Tool:  PC-based configuration software with graphical user interface.

Program:  Overview of Corrigo E settings.

Using E Tool, all settings configured on PC and downloaded into controller.

Infinite number of configurations stored in computer memory for later use.

ASSEMBLY

Factory assemble and wire heat recovery ventilators.

ACCESSORIES

Specifier Notes:  Delete accessories not required.

Shut-Off Damper:  Model EFD and Model AF24 motor.

CO2 Sensor:  Model CO2RT.

Corrigo Repeater:  Model EO-R.

Temperature Sensor (minus 40 to 60 degrees C/IP65):  Model TG-UH/PT1000.

Presence Detector:  Model IR24-P.

SOURCE QUALITY CONTROL

Run test at factory.

EXECUTION

EXAMINATION

Examine areas and supporting structure to receive heat recovery ventilators.

Notify Architect of conditions that would adversely affect installation or subsequent use.

Do not begin installation until unacceptable conditions are corrected.

PREPARATION

Prepare surfaces where heat recovery ventilators are to be mounted.

Ensure surfaces are flat, level, plumb, and can support weight of heat recovery ventilators.

INSTALLATION

Install heat recovery ventilators in accordance with manufacturer’s instructions at locations indicated on the Drawings.

Install heat recovery ventilators in accordance with NFPA 70.

Install heat recovery ventilators level, plumb, and secure.

Do not expose electronic components to temperatures below 32 degrees F (0 degrees C) or above 122 degrees F (50 degrees C).

ADJUSTING

Adjust heat recovery ventilators for proper operation in accordance with manufacturer’s instructions.

DEMONSTRATION

Demonstration:

Demonstrate that heat recovery ventilators function properly in every respect.

Perform demonstration at final system inspection by factory-trained and certified representative of manufacturer.

Instruction and Training:

Provide instruction and training of Owner’s personnel as required for operation and maintenance of heat recovery ventilators.

Provide hands-on demonstrations of operation of system components and complete system, including user-level program changes and functions.

Provide instruction and training by factory-trained and certified representative of manufacturer.

PROTECTION

Protect installed heat recovery ventilators from damage during construction.

END OF SECTION